## Inputs
Inputs from Test Report |  |  |  | Allocate the Load Losses to H, L, T resistances
Winding | H | L | T | Overdetermined on T because tests are done at different MVA levels.
Swdg | 330000000 | 330000000 | 72000000 | Winding | H | L | T
Vwdg | 345000 | 161000 | 13800 | Allocated W | 162795 | 183409 | 62975
Short Circuit Test | HL | HT | LT | Wdg %R | 0.04933% | 0.05558%
Zpu | 0.0723 | 0.2445 | 0.2845 | On reduced MVA for HT and LT tests. Replicate average of HT, LT power.
Pll | 346204 | 225770 | 246384 | MVA ratio | 0.21818 | 0.21818 | 0.21818
Open Circuit Test | H |  |  | HT, LT Losses | 7749.5802 | 8730.8747 | 227836.7726
Pnll | 79267 |  |  | Wdg %R |  |  | 1.45%
Iexc | 0.0407%
Autotransformer SCT winding conversion
OpenDSS Xsc | HL | HT | LT | Ref: Equations 6.44 - 6.50 of EMTP Theory Book
Resistance [pu] | 0.0010491 | 0.00068415 | 0.00074662 | Winding | S | C | T
Reactance [pu] | 0.072292 | 0.2445 | 0.2845 | Vwdg | 184000 | 161000 | 13800
|  |  |  | Swdg | 176000000 | 176000000 | 72000000
OpenDSS Magnetizing Branch Inputs on Winding 1 |  |  |  | Vwdg-1ph | 106232.4495 | 92953.3933 | 13800
%noloadloss | 0.02402% |  |  | Swdg-1ph | 58666666.6667 | 58666666.6667 | 24000000
%imag | 0.03286% |  |  | On reduced Vbase: |  | On reduced Sbase:
|  |  |  | XSC | 0.25415 |  | 0.13555
Check by energizing the transformer from H side, no load |  |  |  | XST | 0.3281 |  | 0.17499
| H | L | T | XCT | 0.2845 |  | 0.15173
Expected Pnll[kW] | 79.267
Ibase[A] | 552.2481 | 1183.3888 |  | Convert core branch to lower Sbase:
Expected Iexc[A] | 0.22476 |  |  | %noloadloss | 0.04504%
Expected Qnll[kVAR] | 108.4247 |  |  | %imag | 0.0616%
Check losses at full load, 1.0 power factor, no fault |  |  |  | Re-use load loss allocations, at lower winding currents:
Check short circuit current with fault |  |  |  | Loss [W] | 162795 | 183409 | 62975
Expected SC Test | HL | HT | LT | Ibase [A] | 552.2481 | 631.1407 | 3012.2623
Expected Pll[kW] | 346.204 | 225.77 | 246.384 | Rwye [Ohm] | 0.17793 | 0.15348 | 0.0023135
Zbase [Ohms] | 360.6818 | 360.6818 | 78.5485 | Zbase [Ohm] | 192.3636 | 147.2784
Expected Isc[A] | 7638.2861 | 2258.6834 | 4159.5387 | Wdg %R | 0.0925% | 0.1042%
|  |  |  | MVA ratio | 0.40909 | 0.40909 | 0.40909
Load flow at full load, 0.85 power factor should match |  |  |  | HT, LT Losses | 27244.6178 | 30694.4814 | 207107.4504
Vload [pu] | 0.9488 |  |  | Wdg %R |  |  | 0.7031%
Vload [deg] | -4.3
Pload [MW] | 329.1
Qload [MVAR] | 204

## Outputs
Model Option: | HLT | 1Bus | 3Bus | AutoTrans | Test Report
Isc-HL [A] | 7620.55 | 7624.45 | 7624.45 | 7620.55 | 7638.3
Isc-HT [A] | 2252.95 | 2253.55 | 2253.55 | 2253.44 | 2258.7
Isc-LT [A] | 4151.36 | 4152.53 | 4152.54 | 4151.36 | 4159.5
Load Loss HL [kW] | 348.775 | 348.77 | 348.78 | 348.959 | 346.2
Load Loss HT [kW] | 237.821 | 223.54 | 223.539 | 223.428 | 225.8
Load Loss LT [kW] | 239.073 | 240.3 | 240.298 | 239.073 | 246.4
Core Loss P [kW] | 79.3 | 79.5 | 79.2 | 79.3 | 79.3
Core Loss Q [kVAR] | 109 | 109.2 | 109.2 | 109.6 | 108.4
Load Vmag [pu] | 0.9488 | 0.94882 | 0.94882 | 0.94878
Load Vang [deg] | -4.3 | -4.3 | -4.3 | -4.3
Load P [MW] | 329.1 | 329.1 | 329.1 | 329.1
Load Q [MVAR] | 204 | 204 | 204 | 204
Notes:
1. Isc-HL consistently low by 0.21%, probably due to drop in switch between Vsource and Transformer
2. The two Dommel transformer models have a "natural" separation in load loss values of HT and LT, like the test report does.
3. The built-in AutoTrans matches test results without the Dommel conversion. It does not explicitly show the smaller MVA size.